New ZFP Tools Testing 21/5/13

Global Changes

- “No.” Should be “Node”

- “Panel Name” should be “Node Name”

- “SEL” removed

- “Nx” to be present above Node Check Boxes

- “Sub Devices” to be changed to just “Devices”

In “Devices” “Pos” should be “Addr” Not done in latest version of Tools

- Panel becomes Node in number column

Structural Changes

- Network View to be System View

- Inside System View Overview to be Network

- “Panel View to be Network View

“Copy to all Panels” to be “Copy to all Nodes” Not done in latest version of Tools

Network View

Overview

- Changes as Dave proposed

Modes

- “ID” should be “Mode”

- Mode IDs to start at 1 not 0

Zones

- “ID” should be “Zone”

Groups

- “Classic” – add “(1st stage, Activated)”

- “Switch” – “(add on, off)”

- “AND” – add “(combinatorial)”

- Default Operational Mode becomes Default Operation

- Modal Overrides to be Modal Operation

Deleting Modes does not delete Modal Overrides Mode entries – Entries are deleted, however, a manual refresh needs to occur.

- In Modal Overrides, change “Overridden Operation Mode” to “Operation”

- Also change “NA” in drop down list to be “Default”

- “ID” should be “Group”

Sequences

“ID” to be “Sequence” Not done in latest version of Tools

- ID numbers to start at 1 rather than 0

Priority – Note to say “(255 = Highest)” Not done in latest version of Tools

Supergroups

Functionality discussed – However, no changes were made.

Pulse Patterns

- “ID” to be “Pattern”

Group Actions

- “ID” to be “Action”

Panel View

- “This panel is a Compact Controller” to go

Icon from AD for non EN54 compliance for Verification Times – After a lengthy discussion it was decided to sideline this proposal as while great in theory in practice complications were likely.

Print Options to read: Not done in latest version of Tools

Fault

Pre-Alarm

Alarm

Disablements

Supervisory Actions

Control Actions

Send/Retrieve Icons need updating Andy D to provide Not done in latest version of Tools

Firmware Versions names to be changed James to get names clarified Not done in latest version of Tools

- Zones Present on this Panel should have Tick Box rather than a 1 or 0

- Device Summary names should be editable as XFP

- Network Filters “Rcv” change to “Accept”

- Panel Notes why blue? – keep as is

Panel View Devices

- Devices 14 and 15 should not be editable

- Panel Keyswitch to be Red

Think of something to address fixed system items To be discussed

Detector Sensitivity

Mode 0,1,2,3 should be 1,2,3,4 Not done in latest version of Tools

Add extra field indicate relating to Detector Modes of Sensitivity not Sensitivity during Panel Modes Not done in latest version of Tools

Cause and Effects

- A  to be changed to AS

“Insert Action” becomes “Insert Action Sequence” Not done in latest version of Tools

“Modal Operation” should not be present on C&E page – Still present, however, now has header text to inform what the drop down box does.

“Insert C and E” to be written long hand Not done in latest version of Tools

Errors  - Errors Tab has been completely removed

Loads long text file

Clean Error button required?

Abus

16 Way I/O Card to be 8/16 Way I/O Card Not done in latest version of Tools

8 Way Relay Card to be 4/8 Way Relay Card Not done in latest version of Tools