Description of the Psuedo Scripting language for changing the configuration of the multi loop panel

Rev : 3

May 2011

Transfer of data to the panel

Currently the 8 loop panel can accept configuration data in an ASCII pseudo scripting type language, as specified in this document.

The data is transferred to the panel using the USB interface

The panel does not need to be put into any special mode for the transfer to take place, but be aware that some changes will require a major re-configuration of data in the panel, and the new stuff may not appear to work straight away.

The PC application required is

ZFPTools.exe

Then choose, Tools, ASCII Transfer.

Multiple files can be selected at once, in which case the files will be sent to the Panel in alphabetical order.

The following record types have special meanings :-

10000	-	when encountered will put the updates into action and re-calculate the file CRCs

etc. The fire panel may not react properly for several minutes after receiving this token while it sorts itself out.

9999	-	Use this token at the end of each download to re-calculate each of the site data

files CRC

9998	-	Use this token at the end of each download to re-calculate each of the site data

files CRC, and also to erase any devices NOT in the download list to Not Fitted.

AFTER 9998/9999 RECORDS ARE SENT, THE PANEL WILL BE NON-RESPONSIVE FOR UP TO 2 MINUTES.

A Special File (ZZ_9998.csv or ZZ_9999.csv) is provided to ensure these procedures will be performed last when downloading multiple files.

Sending to a Networked Panel

After the BEGIN and END tokens, the numeric value (if present) denoted which Panel Number the record will be sent to. If it is not present, the record will be sent to the panel currently connected to the USB.

Device Config.csv

General format

1st column 	-	describes record type

2nd column	-	loop number

3rd column	-	loop address

The record block must always start with a BEGIN token in the 1st field and must end with an END token in the last field.

General device configuration – Record Type = 1

SA0	- Sub-Address 0

SA1	- Sub-Address 1

SA2	- Sub-Address 2

SA3	- Sub-Address 3

Addr		- loop address

Description	- the actual device description text

Type		- device type code

Zone		- device zone

Iso		- isolation group

Flt		- fault group (not currently used)

EventLogMask – Indicates how device events are handled

b7

b6

b5	- 1 DON’T LOG device control actions

b4	- 1 DON’T LOG device supervisory actions

b3	- 1 DON’T LOG device disablements

b2	- 1 DON’T LOG device alarms

b1	- 1 DON’T LOG device pre-alarms

b0	- 1 DON’T LOG device faults

Detector/MCP configuration - Record type = 4

Group		-	output group membership

Action		-	device action when triggered

Sens M0	-	sensitivity in operation mode 0

Sens M1	-	sensitivity in operation mode 1

Sens M2	-	sensitivity in operation mode 2

Sens M3	-	sensitivity in operation mode 3

BS Grp	-	has base sounder in output group

BS add	-	the address of the Base Sounder

Attrib		-	Device attributes

b7	1 – device has remote LED

b6

b5

b4

b3

b2

b1

b0

Sounder Configuration – Record type = 5

Sub addr	-	0 = sounder, 1 = beacon

Zone		-	device zone

Group		-	output group membership

CC group	-	Class Change group membership

Channel	-	0 = sounder, 2 = beacon

Action		-	device action

Mode M0	-	configuration in operation mode 0

Mode M1	-	configuration in operation mode 1

Mode M2	-	configuration in operation mode 2

Mode M3	-	configuration in operation mode 3

b7 	-	1 = polling LED on

b6	-	VOL2

b5	-	VOL1

b4	-	VOL0

b3	-	TONE3

b2	-	TONE2

b1	-	TONE1

b0	-	TONE0

(see Apollo Doc TSD130 for more detail)

I/O Unit configuration – Record type = 3

Sub addr	-	0 – 3

Zone		-	zone association for the sub-address

Group		-	The input group membership

Channel	-	The device channel 0-3

Action		-	Device action

Zone Monitor Unit configuration – Record type = 6

Sub addr	-	0 – 1

Zone		-	zone association for the sub-address

Group		-	The input group membership

Action		-	Device action

User LED configuration data & ABUS General Output configuration – Record type = 7

Group		-	output group membership

SR Stage	-	for SPI-Bus

Identifies which Shift Register the output belongs

For A Bus

Identifies which A Bus device the output belongs

SR Address	-	Identifies the output number on the device

Polarity	-	POS or NEG

User Input configuration data & ABUS General Input configuration – Record type = 8

Group		-	input group membership

SR Stage	-	for SPI-Bus

Identifies which Shift Register the output belongs

For A Bus

Identifies which A Bus device the output belongs

SR Address	-	Identifies the output number on the device

Action		-	device action

Polarity	-	POS or NEG

Zonal LED Configuration data – Record type = 9

NOTE. There can be only 1 Zonal LED  device on the SPI bus

SR Stage	-	for SPI-Bus

Identifies which Shift Register the output belongs

LEDs fitted	-	1 LED fitted for each zone which requires indication

Keyswitch Configuration data – Record type = 10

NOTE. There can be only 1 Keyswitch device on the SPI bus

Group		-	input group membership

Action		-	device action

Polarity		-	POS or NEG

Panel Sounder Configuration data – Record type = 11

OP group	-	output group membership

Sounder	-	which circuit (1 – 4)

Action		-	device action (Usually Gen Output)

Panel Relay Configuration data – Record type = 12

OP group	-	output group membership

Sounder	-	which relay (1 – 4)

Action		-	device action (Usually Gen Output)

ABUS phyiscal device configuration – Record type = 13

Element addr	-	The 1st Element address on Loops_Fitted + 2

(Elements must be consecutively arranged on the loop)

Network addr	-	network address (0 = Local A Bus)

No. elements	-	how many elements the device has

C&E Matrix.csv

General Format

1st column 	-	describes record type

2nd column	-	Input Group number

The record block must always start with a BEGIN token in the 1st field and must end with an END token in the last field.

For each Input Group which has C&E – Record type = 30

Op grp		-	the output group to be actioned

Op seq m0	-	the output sequence when in operation mode 0

Op seq m1	-	the output sequence when in operation mode 1

Op seq m2	-	the output sequence when in operation mode 2

Op seq m3	-	the output sequence when in operation mode 3

The number of OP grp entries is limited to 128

When the specified Input Group is triggered (after satisfying all criteria like dependency, double knock etc), ALL the Output Groups specified in the Row will be actioned with the Output Sequence specified.

Reciprocal Input Groups

When an Input Group has normalized, it may be required to perform a specific action. To enable this, an entry in the C&E matrix with the 2’s complement of the Input Group number will be actioned when that Input Group returns to its normal state.

Activating a Group of Output Groups

If Output Groups have been grouped together (see the G_Groups.csv file), then using the appropriate Special Output Group (2000-2100) in the Op grp field will associated the output sequence with the Group of output groups specified in the G_Group.

IP & OP Group Config.csv

General Format

1st column 	-	describes record type

2nd column	-	Input or Output Group number

The record block must always start with a BEGIN token in the 1st field and must end with an END token in the last field.

Input Group Configuration – Record type = 14

Desc		-	Input group description

Op mode 0	-	operation mode token in operation mode 0

Op mode 1	-	operation mode token in operation mode 1

Op mode 2	-	operation mode token in operation mode 2

Op mode 3	-	operation mode token in operation mode 3

Data0		-	dependent on mode (see below)

Data1		-	dependent on mode (see below)

IG 1st st.	-	Input Group to trigger during 1st stage alarm (0 = none)

auto clear	-	1 = auto clear on panel reset

Delays MCP	-	1 = delays  are applied to MCPs

Delays Det	-	1 = delays  are applied to Detectors

MCP qualifies dep	1 = MCP activation qualifies as a dependency

[Data][Data1]

Op Mode	-	[Data0]			[data1]

Single		-	N/A			N/A

2 Devices	-	1 – must be in the

Same group		N/A

Dep A		-	detector reset time	alarm reset time

(secs)			(mins)

Dep B		-	N/A			alarm reset time

(mins)

Investigation	-	time (secs) for 	N/A

Investigation

period

Output Group Configuration – Record type = 15

Desc		-	Output group description

Silenceable	-	1 = Output group normalizes on Panel Silence

norm on reset	-	1 = Output group normalizes on Panel Reset

disabled	-	1 = Output group disabled (not used)

Output Sequence Data.csv

General Format

1st column 	-	describes record type

2nd column	-	item number

The record block must always start with a BEGIN token in the 1st field and must end with an END token in the last field.

Output Sequences

Pre-delay		- delay in seconds to the Action

Action			- Action to be performed

Action data		- depends on Action

Action			Action data

OP_ON			N/A

OP_OFF			N/A

OP_PreDelay		N/A

OP_Pulse			N/A

OP_Pattern			Pattern number (0 – 8)

OP_Trig_IG			Input group

OP_Trig_NIG		Network input group

OP_Notify			Not used

OP_Trig_Timer		Timer number

OP_Grp_S_ON		Activate group (sounders) in Evac

OP_Grp_S_Pulse		Activate group (sounders) in Alert

OP_Grp_B_ON		Activate group (beacons) in Evac

OP_Grp_B_Pulse		Activate group (beacons) in Alert

OP_Grp_SB_ON	-	Activate group (sounders & beacons) in Evac

OP_Grp_SB_Pulse	-	Activate group (sounders & beacons) in Alert

OP_Grp_OFF	-	turn group off

Timers

Desc			- description of the timer

Type			- timer type token

Triggers IP Group	- input group number

Triggers OP Group	- output group number

OP group sequence	- output sequence

Data0			- dependent on Type

Data1			- dependent on Type

Data2			- dependent on Type

Data3			- dependent on Type

Type		[Data0]		[Data1]		[Data2]		[Data3]

Down Timer	secs to go	N/A		N/A		N/A

Time Of Day	hour		minute		N/A		weekday flags

b7 - spare

b6 – 1 Do Sun

b5 – 1 Do Sat

b4 – 1 Do Fri

b3 – 1 Do Thu

b2 – 1 Do Wed

b1 – 1 Do Tue

b0 – 1 Do Mon

Pulse Patterns

Each stage of the Pulse Pattern lasts for 250mS, there are up to 16 stages in a pattern.

State			- 0 = output off during this stage

1 = output on during this stage

255 = end of sequence, repeat from beginning

Site Config.csv

General Format

1st column 	-	describes record type (always 80)

2nd column	-	Site data record field

The record block must always start with a BEGIN token in the 1st field and must end with an END token in the last field.

Record field and what they are

| 0 = recal time |  |
| --- | --- |
| 1 = maintenance date |  |
| 2 = alarm verification values (det, mcp, IO) |  |
| 3 = maintenance string |  |
| 4 = the panel name |  |
| 5 = mode description texts |  |
| 6 = keyswitch entry version (1 = keyswitch) |  |
| 7 = Total number of HC595 shift register stages |  |
| 8 = Number of actual loops fitted (0 = REPEATER) |  |
| 9 = Language (0 = English, 1 = French etc) |  |
| 10 = Panel Printer mask |  |
| 11 = Panel Loop Protocol (0 = Apollo, 1 = Hochiki) |  |
| 12 = AL2 & AL3 code 13 = Time date yyyy,mm,dd,hh,mm,s) 14 = 1 = Auto DST enabled 15 = LCD auto dimming time (0 = none) |  |

Record field		[data0]		[data1]		[data2]

0			hour		N/A		N/A

1			date		month		year

2			secs(MCP)	secs(DET)	secs(I/O)

3			Maintenance string

4			Panel name

5			mode (0-3)	description

6			1 = keyswitch entry

7			number of SPI-BUS shift registers

8			number of loops fitted (0-7)

9			language (0 = English)

10			printer configuration mask

b7

b6

b5	1 – DO NOT print control actions

b4	1 – DO NOT print supervisory actions

b3	1 – DO NOT print disablement events

b2	1 – DO NOT print alarm events

b1	1 – DO NOT print pre-alarm events

b0 	1 – DO NOT print fault events

11			0 – Apollo, 1 - Hochiki

12			AL2 code	AL3 code	N/A

13			yyyy	mm	dd	hh	mm	ss

14			1 = DST is enabled

15			time (in seconds)

Net Config.csv

General Format

1st column 	-	describes record type (always 120)

2nd column	-	Network data record field

The record block must always start with a BEGIN token in the 1st field and must end with an END token in the last field.

Record field and what they are

| 1 = Network address (seg, add) 2 = Tethered to panel (seg, add) |  |
| --- | --- |

Record field		[data0]		[data1]		[data2]

1			segment	address

2			segment	address

Zone Names.csv

General Format

1st column 	-	describes record type (always 100)

2nd column	-	zone number

3rd column	-	zone name

The record block must always start with a BEGIN token in the 1st field and must end with an END token in the last field.

G_Groups.csv

General Format

1st column 	-	describes record type (always 16)

2nd column	-	Group number (1-99)

3rd column on	-	a list of the Output Groups in the Grouped group

The record block must always start with a BEGIN token in the 1st field and must end with an END token in the last field.

Glossary of Terms

Loops

1-8		- reserved for field devices

9		- reserved for System Devices

10		- reserved for A Bus Elements

11		- reserved for A Bus Devices

Zones

1-200		- reserved for fire zones

205		- system zone for device on the Main Module

206		- system zone for devices on the Peripheral Module

210		- system zone for A_Bus devices

Type Codes

See the Apollo Type code document for Apollo devices

System Devices

PSU           		257

Panel_Sounder 	258

Panel_Relay   		259

User_LED      		260

Input_Device  		261

Fault_Buzzer  		262

Fault_Relay   		263

Event_Log     		264

Panel_Op      		265

Zonal_LED     		266

Keyswitch     		267

PanelPrinter  		268

ABUS device types

16_IO          		300

8_IO           		301

4_SOUNDER      	302

4_ZoneController	303

EndOfDeviceList 	511

Device Action Tokens

NOTE. Tokens MUST match EXACTLY. No leading/trailing spaces etc. are allowed

NONE		-	do nothing

Fire			-	generate a Fire Alarm Condition

NL Fire		-	generate a Non-Latching Fire Alarm Condition

Fault		-	generate a Fault

SuperV		-	Supervisory action (Non-Fire event)

Grp Iso		-	group isolate

Gen Output		-	general Output

C&E Output		-	Special C&E Output (Not currently used)

C&E Input		-	Special C&E Input (Not currently used)

Input Group operation Tokens

NOTE. Tokens MUST match EXACTLY. No leading/trailing spaces etc. are allowed

NONE		-	do nothing

Single		-	single device = fire

2 Devices		-	2 devices = fire (double knock)

Dep A		-	type A dependency mode

Dep B		-	type B dependency mode

Investigation		-	Investigation timer mode

Timer mode Tokens

NOTE. Tokens MUST match EXACTLY. No leading/trailing spaces etc. are allowed

NONE		-	do nothing

Down Timer		-	timer runs to zero, then generates event

Time Of Day		-	timer generates event at time of day

Output Sequence Tokens

NOTE. Tokens MUST match EXACTLY. No leading/trailing spaces etc. are allowed

NONE		-	Do nothing

OP_ON		-	turn output ON continually (Evac)

OP_OFF		-	turn output OFF

OP_PreDelay	-	apply a pre-delay (in seconds)

OP_Pulse		-	simple pulse 1S on/off

OP_Pattern		-	pulse in the specified pattern (1-8)

OP_Trig_IG		-	trigger an Input Group

OP_Trig_NIG	-	trigger a networked Input Group

OP_Notify		-	generate a Notification message (not implemented)

OP_Trig_Timer	-	trigger a soft timer

OP_Grp_S_ON	-	generate a Class Change Group Evac (Sounders only)

OP_Grp_S_Pulse	-	generate a Class Change Group Alert (Sounders only)

OP_Grp_B_ON	-	generate a Class Change Group Evac (Beacons only)

OP_Grp_B_Pulse	-	generate a Class Change Group Evac (Beacons only)

OP_Grp_SB_ON	-	generate a Class Change Group Evac (Sounders & Beacons)

OP_Grp_SB_Pulse	-	generate a Class Change Group Evac (Sounders  & Beacons)

OP_Grp_OFF	-	turn Class Change group off

Signal Polarity Tokens

NOTE. Tokens MUST match EXACTLY. No leading/trailing spaces etc. are allowed

POS			-	signal has POSitive polarity

NEG			-	signal has NEGative polarity

Special Output Groups

1002		-	Change Panel Mode to [Op Sequence]

1003		-	Change Panel Mode to [Op Sequence] (Reciprocal action)

1010		-	Silence

1020		-	Reset

1030		-	ReSound

1200		-	Disable [Op Sequence] Zone

1201		-	Enable [Op Sequence] Zone

1210		-	Disable [Op Sequence] Input Group

1211		-	Enable [Op Sequence] Input Group

1220		-	Disable [Op Sequence] Output Group

1221		-	Enable [Op Sequence] Output Group

1230		-	Disable Sounders in [Op Sequence] group

1231		-	Enable Sounders in [Op Sequence] group

1240		-	Disable [Op Sequence] Device address

1241		-	Enable [Op Sequence] Device address

1250		-	Disable [Op Sequence] Disablement group

1251		-	Enable [Op Sequence] Disablement group

1252		-	Go to AL2

1253		-	Exit AL2

1254		-	Exit ALL access levels

200 – 299	-	Reserved for Grouping of Output Groups

Special Record Types

10000	-	when encountered will put the updates into action and re-calculate the file CRCs

etc. The fire panel may not react properly for several minutes after receiving this token while it sorts itself out.

9998	-	Use this token at the end of each download to re-calculate each of the site data

files CRC, and also to erase any devices NOT in the download list to Not Fitted.

9999	-	Use this token at the end of each download to re-calculate each of the site data

files CRC

Notes on Sounder Groups, Apollo voice sounders, class change etc

It is a requirement to be able to generate a Class Change signal, which is normally different to the evacuation signal. To facilitate this, each sounder can belong to a Class Change group. Members of the same group can be turned on/off using the

Actions in the Output Sequence :-

OP_Grp_S_ON	-	generate a Group Evac (Sounders only)

OP_Grp_S_Pulse	-	generate a Group Alert (Sounders only)

OP_Grp_B_ON	-	generate a Group Evac (Beacons only)

OP_Grp_B_Pulse	-	generate a Group Evac (Beacons only)

OP_Grp_SB_ON	-	generate a Group Evac (Sounders & Beacons)

OP_Grp_SB_Pulse	-	generate a Group Evac (Sounders  & Beacons)

OP_Grp_OFF	-	turn Group off

Because the Apollo Voice Sounders use the same operating principle as their sounder beacons, it is imperative that voice sounders and normal sounders DO NOT occupy the same group. If they did, and the sounders were instructed to turn on with Tone Pair = 3, then any voice sounder in that group would generate a ‘Test Message’ annunciation.

Although the property is termed ‘Class Change’ group, it actually applies to operating the sounder in a Group Mode. It is not strictly reserved for class change operation.

Notes on ABUS devices

When an ABUS device is placed into the system in Loop n+3, the corresponding number of elements MUST be automatically generated in Loop n+2. If an element is not used, its action should be set to NONE.