# Notes

Items in italics have not been developed yet.

All items may be subject to change.

Dimensions are maxima and include PCB standoffs etc.

All field connectors will be pluggable ‘Phoenix’ Type and take up to 1.5 mm CSA wires.

# Cabinets

# Each Module Window can accept two Modules

Standard Shallow for small batteries, 1 x Module Window, 2 x 17 Ah, 450w x 462h x 129d

# Medium Shallow for small batteries, 2 Module Windows, 2 x 17 Ah, 450w x h x 129d

Medium Deep for large batteries, 2 Module Windows, 2 x 38 Ah or 2 x 12 Ah on side 450w x h x 207d

Large Deep for large batteries, 3 x Module Windows, 2 x 38 Ah – 2 x 12 Ah on side, 940h x 450w x 207d

Remote Module cabinet for a display module or indication/switch module, w x h x d

Document box

# Bezels and doors

# Standard Flush metal bezel

Medium Flush bezel metal

Large Flush bezel metal

Standard stainless steel bezel with glazed door

Standard special finish bezel with glazed door

Remote Module bezel (plastic)

# Internal chassis

Stepped Chassis, w x h x d, PSU behind step, one 2-Loop base PCB and one A-Bus PCB

Flat Chassis, w x h x d, one 2- Loop base PCB and three full-size A-Bus PCBs

Mounting Rails for A-Bus PCBs w x h x d

# EN 54-4 PSUs

# Caged for German market but not UK and others

3A EN 54-4, w x h x d

5A EN 54-4, 173w x 143h x 66d

EN 54-4 Remote Module PSU with connector for Hi-Net Daughter PCB

# Modules

# Display module

Features:

# 4.3”, 95x55mm, 472 x 248 pixels, LCD, resistive touch screen

S-Key Key-switch

Mandatory LEDs 1 green, 3 red, 12 yellow

Mini-USB for programming

2 GB Micro SD (max 16 GB)

Ethernet PCB w x h x d

# Up to 3 Indication/Switch Modules per display module – all 160w x 120h x 25d

20-zone Indication Module, name slots & space for 5 switches & 10 LEDs

20-zone Indication Module, name slots, printer* & space for 2 switches & 4 LEDs

# 40-zone Indication Module with name slots

50-zone Indication Module with space for 5 switches & 10 LEDs

# 50-zone Indication Module with printer* & space for 2 switches & 4 LEDs

100-zone Indication Module, numbered 1-100

100-zone Indication Module, numbered 101-200

Blank Module

*Printer Interface/PSU PCB, 75w x 120h x 30d

*Thermal Printer, 80w x 70h x 20d

# Miscellaneous

# Key switch for Module

# Push button for Module

# Base PCBs

2- Loop Base PCB 145w x 160h x 45d

Features

Loop 1 & 2 or loop 5 & 6

Apollo XP95 (126 devices) or Hochiki ESP (127 detectors + 127 sounders) - not both at once

EN 54-4 PSU input

24 VDC 500 mA monitored power output

4 x 1A 6K8 monitored sounder circuits (3A limit),

1 x volt-free general fault relay, 2 x programmable relays – all 1A 24 VDC C/O

# 2 x programmable 6K8 monitored N/O inputs

RS232 pager/DECT port (ability to handle Quantec as well is with Transmitter)

RS 485 A-Bus port

A-Bus power output

2- Loop Daughter PCB (plugs on to 2- Loop Base PCB) w x h x d

Loop 3 & 4 or loop 7 & 8

# A-Bus PCBs (connect to 2-Loop Base PCB or Hi-Net+ PCB)

Cabling is 2 core + screen plus 2-core for power supply, which may be local.

Up to 15 per Network PCB – half-size 80w x 70h x 30d – full-sixe 80w x 150h x 30d

# Powered from 2-Loop Base PCB or other EN 54-4 PSUs

Normally only used within the cabinet(s) but may be extended up to 1 km for non EN 54-2 functions

4 relay PCB (half-size)

8 relay PCB

8 I/O PCB (half-size)

# 16 I/O PCB

# 4 Sounder PCB with PSU monitoring - 4 x 1A 6K8 monitored sounder circuits (3A limit),

# 4 zone PCB (conventional) with 2 sounder circuits and PSU monitoring - 2 x 1A 6K8 monitored sounder circuits

Mimic Interface PCB (will use light guides) How many LEDs – what colours?

# German key box interface PCB

IFAM FAT/FBF PCB German fireman’s panel (Does not connect to Hi-Net+)

# High Integrity Network (Hi-Net)

# Cabling is 2-core + screen, power supply is always local

Max 64 Hi-Net nodes per system

RS 485 Hi-Net Daughter PCB (for 2-Loop Base PCB) w x h x d

RS 485 Hi-Net+ Daughter PCB (For direct connection of A-Bus PCBs) w x h x d

# Interconnects

34-way IDC (Display module to 2-Loop Base PCB)

6-way IDC (Display module to Printer Interface/PSU)

8-way IDC (Display module to Indication/Switch Modules)

# PC Software

# PC Tools – English

# PC Tools – other languages

# PC Logging software for end users

# Features

# Very user-friendly colour LCD touch-screen interface

Very complex cause and effects possible

Micro SD memory can be removed for off-site configuration

# Programming via USB port on display module

Thermal printer paper can be loaded without opening the cabinet

# The printer assembly can be replaced without opening the cabinet

# The LCD will identify the product version when in alarm state to aid tech support

# Installer logo, name, phone and web address can be shown on the LCD

# Real Time Clock has automatic daylight saving function (BST/GMT etc.)

20,000 filterable event memory (fire, fault, system event)

Simple selection of supported languages – currently English with German to follow)

Slide-in label system and templates for indication and switch modules

# Internet connectivity

# Internet connection via optional Ethernet port PCB

Internet functionality TBA but the following are being considered.

# Emailing of events

Ability to review programming, cause and effects and alarm status

If provided, the ability to make changes remotely will still require a site engineer

# Configuration

# Full functionality will require the PC Tools

Functions available from the display module will include:

Loop learn

Add/modify/remove device

Show fitted devices

# Repeaters and remote modules

The cabinet for remote modules and repeaters has not been designed yet.

However, they will be shallow and power will either come from the panel or a local EN 54 PSU – diverse power routing may be needed..

# Minimum configuration

# Standard cabinet, 3A PSU, 2 loops, no printer, blank module

# Standard configuration

Standard cabinet, 3A PSU, 2 loops, no printer, 40-zone indication module with name slots

# Limits to configurations

# Max 4 loops in standard cabinet

Max 8 loops in one cabinet

Max 512 detectors or MCPs under the control of one microprocessor (Display module) – this can fail as long as at least one mandatory output operates (Fire Alarm output (sounder), Fire protection output (shutter, fan), fire routing output (communicator)).

Therefore, for an 8-loop panel, this is an average of 64 per loop.

Max 64 Hi-Net nodes

Max 512 loops

Simple safe configuration limits will be defined

Absolute limits are mainly a function of power supply and loop current limits.

The PC Tools will have traps to warn when limits are reached.

# Documents

# Specifications

Installer Manual – English

Installer Manual – other languages

User manual – English

User manual – other languages

Promotional tools

# Packaging

# Standard Cabinet shallow

Medium Cabinet shallow

Medium Cabinet deep

Large Cabinet deep

Standard Flush Bezel

Medium Flush Bezel

Large Flush Bezel

Module Bezel

Internal Chassis (flat and stepped)

Module and 2-Loop Base PCB

A-Bus PCB (Full and Half size)

Hi-Net, Hi-Net+, 2-Loop Daughter, Ethernet

Switches

# Setting up the MK1 demo system

Connect ZFP blue/yellow to Loop 1 on SIM system.

Connect PC to ZFP (USB port on right nearest PC screen)

# Connect power to all

Set clock via Menu/Access Level 2 (2222) or a fault will show (RTC has short life)

Open “4 Loop demo ASY”

Trigger an alarm in the SIM system

To change the names of zones – Menu/Access Level 3 (3333)

The key-switch is programmed to disable zone 1