Edited 7/8/13 by AR

Original: 25/6/13

¦ Anthony Roberts

DRQ141 : “DRAX Interface”

Doc No. DRQ141-000100

| C-Tec |  |
| --- | --- |

Basic protocol

The basic protocol over which data will be transferred will be :-

RS232

19200 BAUD, 8 data, 1 start, 1 stop bit, No Parity

If the distance between the DRAX workstation and the panel is too great for RS232, then a DRAX recommended RS232/RS485 convertor will be used in the 1st instance. It may be possible to utilize a spare RS485 port directly from the panel.

The packet format we propose is an ASCII packet with BINARY framing characters :-

<SOH>[rt]{len hi, len lo}[seq](“DATA”){chk hi, chk lo}<EOT>

<SOH>	-	BYTE	-	ASCII character 1

[rt]		-	BYTE	-	record type	(1 = ASCII “DATA”, 0 = BINARY DATA)

len		-	WORD	-	number of characters in (DATA) payload

seq		-	BYTE	-	incrementing binary sequence number

chk		-	WORD	-	sum of all characters from <SOH> to the last byte in

(DATA) inclusive

<EOT>		-	BYTE	-	ASCII character 4

The [seq] field

This field is included to improve the interface robustness. In all communication dialogs, there will always be a generated message and an acknowledgement message. For every generated message, the [seq] field will increment. For every acknowledgement message, the [seq] field will be the same as the generated message being acknowledged.

General dialog Protocol

Either the panel or the PC can generate a message, with neither being ‘The Master’.

Each message dialog will consist of a generated message (GM) and acknowledgement message (AM).

A GM message will expect a corresponding AM message within 100mS.

A GM message will be re-sent up to 5 times before being discarded.

DATA packets

DATA will be in the form of an ASCII, Comma Separated Values (CSV) string. This will make it easy to interpret using basic debugging tools such as terminal programs etc. It is possible for some fields to be empty.

Data fields

(fields in italics are not specifically required by DRAX)

Site		-	string which describes the site

Eg. “C-Tec R&D”

Panel no.	-	The panel number originating the message

Eg. “P:01”

Time/Date	-	The time and date of the message (eg. Event). The time will

always be represented in 24 hour format.

Eg. “01/08/2013 11:56:00”

DST Flag	-	Flag to indicate if Daylight Saving Time is applied.

Eg. “0” (not applied) or “1” (applied)

Packet Type	-	Type of packet

Eg. 	“PT:00”	Event Packet

“PT:10”	Control Packet

“PT:20”	Handshaking Packet

Each Packet Type will now have further ASCII CSV fields, as described :-

EVENT Packet (Packet Type = “0”) additional fields

Loop		-	The loop which generated the event message. In the case where

the event is not associated with a Device, then the value will be

zero.

Eg. “L:01”

Device no.	-	The Device which generated the event message. In the case

where the event is not associated with a, then the value will be zero.

Eg. “D:123”

Device Type	-	The Device Type which generated the event message. In the case

where the event is not associated with a Device, then the value will be NULL (i.e. “”).

Eg. “XP95 Optical”

Zone no.	-	The Zone no. which generated the event message. In the case

where the event is not associated with a Device, then the value will be zero.

Eg. “Z:123”

Zone name	-	The Zone Name which generated the event message. In the case

where the event is not associated with a Device, then the value will be NULL (i.e. “”).

Eg. “Ground Floor”

Device name	-	The Device Name which generated the event message. In the

case where the event is not associated with a Device, then the value will be NULL (i.e. “”).

Eg. “Reception Void”

Event Type	-	A numeric token representing the type of event (See Event List).

Eg. “E:25”

Event Parameters	Zero or more fields denoting a token or value. The exact format of these fields will be dependant upon Event Type

Example Packet

e.g. A Fire event from C-Tec R&D, panel 1, loop 1, device 123, zone 123 :-

“C-Tec R&D,P:01,01/08/2013 11:56:00,0,PT:00,L:01,D:123,XP95 Optical,Z:123,  Ground Floor,Reception Void,E:21”

Handshaking Packets (Packet Type - “20”) additional fields

“ACK,chk”	-	chk is the ASCII decimal representation of the associated GM’s

checksum

“NAK,chk”	-	chk is the ASCII decimal representation of the associated GM’s

checksum

“CSFAIL”	-	the checksum of the associated GM was not correct

Control Packets (Packet Type - “10”) additional fields

Control Type	-	A numeric token representing the type of Control (See Control

Type List).

Eg. “C:25”

Control Parameters	Zero or more fields denoting a token or value. The exact format of these fields will be dependant upon Control Type

Control Type List and Additional Fields

“100”		-	Request Overall status from panel

No additional fields

e.g. To request the current general overall status from a panel, the PC would send :-

“C-Tec R&D,P:01,,0,PT:10,100”

Event List

“001”	-	Device Ok

“010”	-	Device in Fault

“020”	-	Pre-Alarm

“021”	-	Fire

“022”	-	Test Alarm

“030”	-	Device disabled (isolated)

“031”	-	Device enabled

“040”	-	Zone disabled (isolated)

“041”	-	Zone enabled

“100”	-	Panel Muted

“101”	-	Panel Silenced

“102”	-	Panel Reset

“200”	-	Output Group activated

“201”	-	Output Group normalized

Example dialogs

These examples show only the ASCII Data payload part of the complete packet. Where an “ACK” type control packet is described, the ASCII checksum “1234” is only a representation of the value and the actual value will be different.

PC requests General Status :-

PC  Panel : “C-Tec R&D,P:01,,0,PT:10,100”

Panel  PC : “C-Tec R&D,P:01,,0,PT:20,ACK,1234”   (1234 is a representative number!)

Panel generates a Fire Event :-

Panel  PC : “C-Tec R&D,P:01,01/08/2013 11:56:00,0,PT:00,L:01,D:123,XP95 Optical,

Z:123,Ground Floor,Reception Void,E:21”

PC  Panel : “C-Tec R&D,P:01,,0,PT:20,ACK,1234”   (1234 is a representative number!)

PC generates a Silence Event :-

PC  Panel : “C-Tec R&D,P:01,,0,PT:10,10”

Panel  PC : “C-Tec R&D,P:01,,0,PT:20,ACK,1234”   (1234 is a representative number!)

Or (Using a type “00” Event Message)

PC  Panel : “C-Tec R&D,P:01,01/08/2013 11:56:00,0,PT:00,L:0,D:0,,Z:0,,,E:101”

Panel  PC : “C-Tec R&D,P:01,,0,PT:20,ACK,1234”   (1234 is a representative number!)

Panel generates a Silence Event :-

Panel  PC : “C-Tec R&D,P:01,01/08/2013 11:56:00,0,PT:00,L:0,D:0,,Z:0,,,E:101”

PC  Panel : “C-Tec R&D,P:01,,0,PT:20,ACK,1234”   (1234 is a representative number!)