ZFP Overview

ZFP is a range of EN 54-2/4 fire alarm control panels that can be configured with two, four, six or eight Apollo XP95 / Discovery addressable loops.

Adding a network PCB allows each control panel to be a network node.

Up to 128 nodes can be connected in a ring on a high-integrity bi-directional RS485 network (Hi-Net) with up to 64 control panels and up to 64 other network devices such as compact controllers, repeaters and A-Bus controllers.

(For legacy projects, up to 8 nodes can be connected in a “daisy-chain” on a singe path network (S-Net)).

A ZFP panel can control to up to 1024 (512?) fire alarm devices or manual call points and so a network of panels can have up to 65536 (32704?) fire detectors or manual call points. Each panel can also have up to 200 detection zones and so it is possible to have a system with up to 12800 detection zones.

This means that setting up the “cause and effects” can be very complicated, particularly when considering delays and dependencies to outputs and controlling escape doors, smoke extraction etc. This becomes even more difficult to manage in real installations where the configuration often changes many times before, and after, the system is handed over.

ZFP Configuration Concept

## Zones

It is normal to manage the cause and effects of a fire alarm control panel in relation to the detection and alarm zones defined in EN 54.

EN 54-1 defines a zone as "a geographical sub-division of the protected premises in which a function may be carried out separately from any other sub-division". The functions are the automatic fire detection function (A), the manual initiating function (B) and the fire alarm function (C).

In EN 54-2, zones are the mandatory units for the indication of fire alarms. The main aim is to provide unique indications for the zone(s) in which fire alarms originate, so that a multiplicity of alarm signals from fire detectors in one volume do not clutter an alphanumeric display and risk preventing the rapid recognition of new zones in alarm.

Two types of zone are referred to, input (or detection) zones, which contain fire detectors and manual call points and output (or alarm) zones, which contain devices such as sounders and beacons (VADs).

Input zones may be sub-divided so that signals from individual input devices or groups of input devices smaller than one input zone may be identified at the CIE. This provides more detailed information on the location of an event, in addition to the indication of the affected zone.

However, input zones are not ideal tools for setting up the cause and effects because, although they provide geographical information to locate the source of a fire or a fault, they often do not relate directly to the different effects that need to occur that depend on signals from individual devices or groups of devices within or across input zones.

A simple example is a building where any MCP in any zone needs to trigger all sounders immediately, whereas any fire detector will start a delay timer to allow time for investigation.

Similarly, although output zones are essential for grouping alarm sounders and VADs geographically, they are not useful for controlling other output devices such as escape doors, smoke extraction equipment etc.

A simple example is………?

## The ZFP Way

Although the ZFP has input and output zones as required by EN 54, a different system, called DIOSAC, which is much simpler to manage, is used to handle the cause and effects.

DIOSAC uses the concept of ‘Devices’ ‘Input Groups’, ‘Output Groups’, ‘States’, ‘Actions’ and ‘Cause and Effects Function’ as described below to allow devices to be grouped in sets that can then be manipulated logically. Changes to individual devices are easily managed by adding or removing them from the sets..

### Devices

There are four classes of device.

Field Input Devices (FID) – Fire Detectors, MCPs, Zone Monitors, Input Units. Each FID belongs to one input (detection) zone but also belong to one Input Group.

Panel Input Devices (PID) – Keyswitches, Touchscreen, Main 2-Loop PCB inputs, A-Bus inputs. Each PID belongs to one Input Group.

Field Output Devices (FOD) – Sounders, VADs, Output Units. Each FOD belongs to one output (alarm) zone but also belong to one Output Group.

Panel Output Devices (PDO) – Panel LED, Display Text, Sounder Circuits, Main 2-Loop PCB Outputs, A-Bus outputs. Each POD belongs to one Output Group.

### Cause and Effects Function (CEF)

CEFs have a unique number but can also be named – e.g. in a fire alarm connected to a voice alarm system, a CEF might be called ‘Voice Alarm C&E’.

### Input Groups

IGs have a unique number but can also be named – e.g. in a small staged-alarm system IG1 might be called ‘Fire Detectors’ and IG2 might be called ‘MCPs’

### States

IGs are linked to ‘States’. Default states are on, off, pulsing

### Actions

### Output Groups

OGs have a unique number but can also be named – e.g. in a theatre with staff pre-alarm OG1 might be called ‘Beacons’ and OG2 might be called ‘Sounders’.

### Modes

The modes function is used when panels are networked. Typical Modes are “All panels” or selected panels.